Specification for Installer Friendly Series® Single Phase Control Panel

1.	Must be available in either simplex or duplex models.
2.	Incoming pump power shall be single-phase, 60 Hz, 120/208/240 volts AC.
3.	Incoming control/alarm power shall be single-phase, 60 Hz, 120 volts AC.
4.	Easy to use touch pad for programming pump control.
5.	The control panel is to have models available that interface with float input and models available that interface with transducer input.
6.	Float-operated models shall incorporate three (3), or four (4), normally open, mercury or mechanically-activated control switches with pipe clamps. Inputs shall be labeled in the panel as stop, lead, lag/alarm, and alarm for demand dose and redundant off, timer enable, high alarm, and timer override (timed dose models). Floats shall be SJE-Rhombus control switches or approved equal.
7.	Transducer-operated models shall incorporate SJE-Rhombus C-Level™ sensor.
8.	The control panel is to have a means to be configured in the field to operate as either a time dose or demand dose panel.
9.	The control panel is to be equipped with separately fused alarm and control circuits.
10.	The control panel is to be equipped with float status indicators, pump run indicators, Hand – Off – Auto status indicators, and power on indicators.
11.	Panel must log the following data: Pump run time, cycle counts, alarm counts, float out of sequence counts, and timer override counts (time dose only).
12.	Alarm must activate if floats operate out of sequence (float model) or if transducer circuit opens (C-Level™ sensor model).